December 11, 2017

Attn: Len Swartz, P.E.

Olsson Associates

2111 S 67th St. Suite 200

Omaha, NE 68106

RE:  PAD 5 AT SUMMIT FAIR

Dear Mr. Swartz:

Upon review of the waiver request provided to the City on October 20, 2017, staff has issued a final determination.

There were three key issues identified with the relocated sanitary sewer line.  None of the deviations were reflected on the original set of approved plans, and plans were not submitted for review prior to construction.  It is understood that site conditions made the original design infeasible; therefore, changes were made in the field.  This resulted in the sanitary sewer not being constructed in accordance with the City of Lee’s Summit Design and Construction Manual (DCM).

The installed slope of the sanitary sewer main does not meet the standards found in the DCM.  The flow data was reviewed, along with your written waiver request, and it has been determined that the line will be allowed to remain in place, as is.  Although it does not meet the minimum standard, it has been determined that the current flow conditions present in the main are adequate to allow the pipe to remain.

The minimum drop across manhole inverts does not meet the standards.  The flow data was reviewed and it was determined that the inverts will be allowed to remain in place, as is.

A ‘doghouse’ manhole was constructed on the main, which is not an approved manhole.  These types of manholes are not allowed due to the enhanced possibility of infiltration into the system. It has been our experience that they do not provide a seal tight enough to ensure infiltration does not occur.

It has been determined that this manhole will have to be replaced with a compliant manhole.

Thank you for working with us in ensuring that we bring the project into compliance by meeting the intent of the standards.  If you have any questions in regards to these findings, please feel free to contact me.

Sincerely,

Ryan A. Elam, PE

Director of Development Services

cc:	  George Binger, P.E., City Engineer

Kent Monter, P.E., Development Engineering Manager

Mark Schaufler, Director of Water Utilities

Jeff Thorn, P.E., Assistant Director of Engineering Services, Water Utilities