December 1, 2014

Fairway Construction Company Inc

206 Peach Way

Columbia, MO 65203

Attn:  Matt Perry

Matt,

This letter is to provide you with a list of items that either need to be completed or corrected prior to receiving a full certificate of occupancy for this project.  Here are the items identified by the Codes Administration Division.

General

- Get approvals from all departments: Water, Public Works, Fire and Planning and Development

- Final special inspections approval.

- Submit elevator certificate.

Complete exterior:

- Downspots

- Dryer dampers

- All exterior wall finishes

- Repair/seal exterior joints

- Exterior lighting and receptacle outlets

- Secure LFNC whip within 12” of elevator

- A/C unit disconnect

- Label service meter

Service building

- Anchor sill plates per plans

- Complete the electrical to the building

Rooftop

- Install weather proof covers for all receptacles

- Secure all LFNC within 12” of disconnects

Interior

- Complete interior commons areas.  Commons areas and areas other than dwelling units have not been inspected

- All stair handrails shall be able to withstand 200 pounds of concentrated force

- Add support brackets to handrails that haven’t sufficient support brackets

- Corridor above ceiling air handling units shall have disconnect within sight

- Adjust the door at the stair enclosures to no more than 5 pounds closing force

- Install door latches where not installed on stair enclosures

- Provide smoke and draft control for all doors in accordance with UL 1748 and labeled accordingly

- Adjust all doors that do not self close properly

- Make sure all doors are labeled

- Install accessible signage at stair entry doors and inside

- Tactile signage for areas of refuge also comply with 1007.6.5/A117.1

- Area of refuge two way communication

- Required minimum 6’-8” headroom clearance above stair at NE stair enclosure near top level

- Install handrails on both sides for stairs to rooftop

Dwelling units

- Firecaulk all penetrations or ceiling holes in mechanical space at end units and unit 312

- GFCI protection for kitchen counter receptacles near range in ADA units

Please feel free to contact me or the inspections staff with any questions you may have.

Sincerely,

Mike Weisenborn

Project Manager

Lee’s Summit Development Center

816-969-1240

Mike.weisenborn@cityofls.net